## Slide 1: EG4 6500 Firmware 61.13 & 79.71 N-G Bond

## Slide 2
This power point will help you test for the N-G bond setting for EG4 6500.

## Slide 3
First you will power on the inverter by pressing the power button. Once the inverter is on, hold the fault button on the bottom right corner of the face plate for 3-5 seconds for the setting menu to show.

## Slide 4
Scroll up using the top arrow until you get to setting 42 to select the N-G bond setting.

## Slide 5
In this setting you can choose to enable (ENA) or disable (DIS) the N-G bond in your inverter.

## Slide 6
To disable the N-G bond select ENA on the screen, then exit out to the home screen then turn your inverter off and on. To make sure the setting sticks use a multimeter to check for continuity between the N & G terminal on the AC Output. If you select the ENA setting than your multimeter should read OL .

## Slide 7
To enable the N-G bond select DIS on the screen, then exit out to the home screen then turn your inverter off and on. To make sure the setting sticks use a multimeter to check for continuity between the N & G terminal on the AC Output. If you select the DIS setting than your multimeter should read 0.1.

## Slide 8
If you follow these steps you should be able to select your N-G bond setting with no issues.